## Slide 1
Large-scale Commercial Heat Pump Water Heaters

## Slide 2
Unit Design
  Electrically-driven
  Uses refrigeration cycle
  Air or water source
  Direct heating of potable water

## Slide 3
System Design
  Pair with storage tanks
  Store at 140ºF-160ºF and mix down

## Slide 4
Large-scale Applications
  Multifamily
  Hotels
  Dormitories
  Barracks
  Schools
  Net Zero
  Passive House
  LEED

## Slide 5
Benefits of HPWHs
  Electrification
  High Efficiency [COPs of 1.5 - 6]
  Free cooling or heat recovery
  Load shifting, night operation
  No exhaust piping or waste streams
  Low Maintenance

## Slide 6
Sizing New HPWH Systems
  Longer runtimes, lower GPH recovery
  Pair with storage for peak load
  Select units for lowest design temperature
  Stage off units during warmer months

## Slide 7: Required Design Information
  Source type
  Min and max source design temperatures
  Water temperatures (Supply, stored, mixed)
  Building/usage type(s)
  Total daily usage and peak hour usage (or building details)
  Building loop losses (btuh)

## Slide 8: Total Daily Usage Sizing
  Estimate Occupancy
  ASPE/ASHRAE Daily Usage Per Person
  HPWH Required Recovery = Daily Usage / Desired Run Hours
Notes: Combine heat pumps with storage to reduce equipment size
Daily recovery rather than hourly
Heat pumps cover total daily usage, tanks provide for peak loads

## Slide 9: Daily Usage Profiles
  Hourly Load Profile or Peak 4 hr usage to size storage
  Size loop heater unit and recirc. tank to match recirc. losses
Notes: Combine heat pumps with storage to reduce equipment size
Daily recovery rather than hourly
Heat pumps cover total daily usage, tanks provide for peak loads

## Slide 10: Single vs Multi Pass Heating
Internal
Pump
E-TCV
Notes: E-TCV valve is what we do differently
Meters domestic water flow, 100 degree lifts, constant output temperature
Circulator pump to tanks and back

## Slide 11
Multi-pass Operation
  Higher flow, low lift
  Constant flow rate
  Varying output temperature
  Recirc. loop heating and retrofits
HPWH
Cold Supply
TMV
T+10°F
T
50 -140°F

## Slide 12
Single pass Operation
  Lower flow, high lift
  Constant output temperature
  Varying flowrate
  Minimum lift required
  Size pipes for max flow rate
HPWH
Cold Supply
140°F
TMV
140°F
50-120°F
140°F

## Slide 13
Stratified storage, Series tanks
HPWH
COLD
SUPPLY
140°F
TO
MIXING
VALVE
140°F
140°F

## Slide 14
HPWH System Piping
COLD
SUPPLY
To Mixing
Valve
STORAGE
TANK
STORAGE
TANK
HPWH
LEAD
HPWH
HPWH
EXP

## Slide 15
Recommended unit fittings

## Slide 16
Recirc. Return Options

## Slide 17
Recirc. Return Options
Return To Tanks
140°F
Return Water
110°F
To Building
120°F
Cold
Aquastat
TMV
< 120°F
<20%

## Slide 18
HPWH System Piping
COLD
SUPPLY
140-170°F
HWR
MIXING
VALVE
RECIRC
TANK
STORAGE
TANK
STORAGE
TANK
110°F
120-170°F
HPWH
LEAD
HPWH
HPWH
HPWH
EXP

## Slide 19
Retrofit Considerations
  Meter usage and losses
  Leave old equipment?
  Electrical service limitations
  Single or multi-pass

## Slide 20: New Cx Series
Common control program across all models
PLC, touchscreen, EEVs standard
304L stainless cabinets standard
Interconnecting controls, 8 units staging and runtime balancing
Up to 30 hp compressors

## Slide 21: New Cx Series
Trends temperature history for 10 days
Download run data to USB
Upload new code updates from USB

## Slide 22: Cloud-Based Monitoring
  Free cloud data logging (1 year rolling)
  Email and text alerts
  Remote monitoring and troubleshooting
  One module required per array

## Slide 23: CxV-5: Air Source
4 Nominal Tons (48 MBH)
Prop fan only (not ECM)
Swing-open front panel for servicing
Defrosts Required
50°F (13C)
100°F (38C)
10°F (-10C)
-4°F (-15C)
140°F Output
120°F Output

## Slide 24: CxA-10 to -30: Air Source
10 – 25 Nominal Tons (120 – 300 MBH)
ECM fans, axial or plenum
2-3 in static with plenum fan
Electrocoated evaporators
Reduced footprint

## Slide 25
CxA: reduced footprint

## Slide 26: CxA: Air Source
Zero side clearance required
Slide-out tray for refrigeration component access

## Slide 27: CxA Operating Range
95°F (35C)
120°F (49C)
35°F (2C)
28°F (-4C)
Defrosts Required
50°F (13C)
140°F
Output
120°F
Output
High Temp Compressor

## Slide 28: CxA: Air Source

## Slide 29: CxW: Water Source
9 – 25 Nominal Tons (108 – 300 MBH)
Single compressor / circuit
Stackable
Optional single point electrical and interconnecting headers

## Slide 30: CxW Reduced Size

## Slide 31: CxW Operating Range
85°F (29C)
High Temp Compressor
110°F (43C)
45°F (6C)
Notes: Source temps down to 20F if source fluid allows

## Slide 32: Staging Controller

## Slide 33: Packaged Skids
  Colmac piping method and required plumbing components
  Factory assembled and tested
  Copper, Stainless or Aquatherm

## Slide 34: Packaged Skids
  Copper, Stainless or Aquatherm
  Other specified components
  Master controller for entire hot water system

## Slide 35: Additional resources available at colmacwaterheat.com

## Slide 36
HFC Refrigerants
    R-410a GWP: 2,088
    R-134a GWP: 1,430
    Common components and servicing
    Phasing out to HFO replacements

## Slide 37
Natural Refrigerants
    R-744 (CO2) GWP: 1
    R-717 (Ammonia) GWP: 0
    R-290a (Propane) GWP: 3
    Low-temperature operation
    Limited components and servicing
    Pressure, flammability, toxicity

## Slide 38
HFO Refrigerants
  R-1234yf GWP: 1
  R-1234ze GWP: 1
  Currently limited component availability
  Flammability: A2L, A3 Classifications